## Slide 1
PROJECT DETAILS |  |  |  |  |  |  |  |  | 
NAME: 3-Bedroom Detached House Show Home |  |  |  | SITE ADDRESS: <site address> |  |  |  | CLIENT NAME: <client name> | 
CONTRACTOR DETAILS |  |  |  | 
NAME: <contractor’s name> | ADDRESS: <contractor’s address > | PHONE |  | E-MAIL: <contractor’s e-mail>
 |  | office: <###> | mobile: <###> | 
GENERAL INSTRUCTIONS and PREPATORY NOTES | 
1/ | Please review this specification, the reference drawings and schedules and contact me as soon as possible with any issues or questions.
2/ | This specification is organized in a room-by-room format (a separate section is provided for each room/area, with the 2 outdoor spaces grouped together at the end).
3/ | This specification includes all lighting components that require installation by a qualified electrician, including the type of control mechanism / switch to be used in each case -- as marked on the Reflected Ceiling Plans (Ground and First Floor). Light switches are to be installed at standard height (guideline used: 1200 mm to top of plate) unless otherwise noted.
4/ | This specification lists all electrical components as marked on the Electrical Plans (Ground and First Floor) along with relevant notes, incl. item height. (Standard height guideline used: 400-450 mm to mid-plate.)
5/ | Fitted (not readily portable) lighting components that are not to be hardwired and that may be installed by the decorators (i.e. that do not require installation by a qualified electrician) are also included for clarity and noted as such under ADDITIONAL INFO for each room/area.
6/ | Portable table and floors lamps are not included in this specification document, but lamp sockets in appropriate locations to accommodate for these lights to be plugged in are listed and also specified on the Electrical Plan drawings. These plug-in light fittings are drawn on the Furnishing Layout Drawings (Ground and First Floor).
7/ | Important notes for scheduling/coordinating with the flooring and painter/decorator / kitchen contractors: All concealed electrical wiring is to be done ahead of relevant flooring and wall covering installations. For the installation of the floor electrical sockets in the Sitting Room: Wiring is to be concealed underneath the hardwood floor. Please coordinate closely with the flooring contractors for this custom installation. The under-cabinet kitchen lighting is to be installed onto the bottom sides of the wall cabinets after they have been hung. However, please account for any wall cable concealment to be done prior to the application of the wall finish, which is to be done prior to the cabinets’ installation. Please advise ahead of time of all anticipated jobs so that appropriate sequencing of tasks can be coordinated between all contractors.
8/ | Please ensure that the lighting scheme is electrically sound with no circuit overloads nor any other technical issues. Please ensure all installations are compliant with current regulations. Please propose any necessary modifications and/or improvements (i.e. suggest appropriate switch panel solutions to accommodate groupings of light switches etc.) in a timely manner. Any recommended changes will require to be agreed upon before implementation.
9/ | The specific manufacturer’s instructions are to be followed in each case.
10/ | As much as possible, please leave the work areas in a tidy fashion at the end of each day. All rubbish is to be promptly removed from the site.
MAIN DETAILS

## Slide 2
HALL, STAIRS AND LANDING
LIGHTING |  |  |  |  |  |  |  |  |  |  | 
Ref ID within room | TYPE | BRAND / SUPPLIER | NAME | QUANTITY | CODE / REF | COLOUR/FINISH OPTION | DIMS (mm) | BULB | CONTROL SWITCH | REFERENCE DRAWING | ADDITIONAL INFO and WWW LINKS
6 | Pendant Uplighter | John Lewis | Easy-to-fit Ida Uplighter | 4 (2 for Hall and 2 for Landing) | 149222 | Cream Fabric | 350W x 350D x 170H Drop 350 | Max 60W Standard (not included) | The 2 pendant uplighters in Hall and the 2 pendant uplighters in Landing to be on separate circuits, each using: dimmer switches for lighting control from 3 different locations (as shown on drawings) | (D16) Reflected Ceiling Plan – Ground Floor (D17)Reflected Ceiling Plan – First Floor | Product info: http://www.johnlewis.com/john-lewis-easy-to-fit-ida-uplighter-shade/p149222
7 | Wall Sconce | Philips Forecast Lighting / YLighting | Nienke 1 Light Wall Sconce | 8 (3 for Hall, 2 for Staircase, 3 for Landing) | 360621748 | Nickel with Etched Glass | 285.75(11.25”)W X 228.6(9”)H X 120.65(4.75”)extension | 1 X 60W 120V E26 (medium base) A19 incandescent lamp (not included) | The 3 sconces in Hall and the 3 sconces in Landing to be on separate circuits, each using: dimmer switches for lighting control from 3 different locations (as shown on drawings); The 2 Staircase sconces to have their own circuit using dimmer switches for lighting control from 2 different locations (as shown on drawings) | (D18) Electrical Plan – Ground Floor (D19) Electrical Plan – First Floor | Product info: http://www.ylighting.com/philips-forecast-lighting-nienke-1-light-wall-sconce.html Height for sconces installation: 1750 mm
*Note: Under-stairs built-in storage lighting is not included in this specification document. The lighting concept/suggestion for this unit is included in the Under-stairs Built-in Storage Concept document.
ELECTRICAL |  |  | 
DESCRIPTION | QUANTITY | REFERENCE DRAWING | ADDITIONAL NOTES
Double switched socket outlet | 2 | (D18) Electrical Plan – Ground Floor, (D19) Electrical Plan – First Floor | Standard height
Single switched socket outlet | 1 | (D18) Electrical Plan – Ground Floor | Standard height

## Slide 3
STUDY
LIGHTING |  |  |  |  |  |  |  |  |  |  | 
Ref ID within room | TYPE | BRAND / SUPPLIER | NAME | QUANTITY | CODE / REF | COLOUR/FINISH OPTION | DIMS (mm) | BULB | CONTROL SWITCH | REFERENCE DRAWING | ADDITIONAL INFO and WWW LINKS
16 | Flush Mount Ceiling Light | Philips / Ylighting | Ecomoods Ceiling Light | 1 | 326104848 | Aluminum | 350.52(13.8”)Dia. X 50.8(2”)H | 1 x 40W 120V 60Hz 2GX13 base Circline Fluorescent (included) | Not dimmable. On/Off switch positioned at entry point | (D16) Reflected Ceiling Plan – Ground Floor | Product info: http://www.ylighting.com/philips-luminaires-ecomoods-1-light-32610-ceiling-light.html
17 | Cabinet Spot Light *See ADDITIONAL INFO >>>>>>> | IKEA | GRUNDTAL Spot Light | 6 (2 packs) | Article Number : 501.283.84 | Nickel Plated | Diameter: 6.6 cm Height: 2.8 cm Cord length: 350 cm | Halogen bulb G4 12V 10W (included) | Included with each package. To be plugged into lamp sockets controlled by a wall switch (as shown on drawing) | Lamp sockets shown on (D18) Electrical Plan - Ground Floor | Product info: http://www.ikea.com/ca/en/catalog/products/50119351/#/50119351 Not to be hardwired. 4 inside the GALANT wall cabinet, and 2 inside the GALANT storage combination with roll-front, equally spaced as shown on the Study Concept Board. May be installed by the decorators (included here for clarity).
ELECTRICAL |  |  | 
DESCRIPTION | QUANTITY | REFERENCE DRAWING | ADDITIONAL NOTES
Double switched socket outlet | 3 | (D18) Electrical Plan – Ground Floor | Standard height
Single lamp socket outlet (controlled from wall switch) | 2 | (D18) Electrical Plan – Ground Floor | Standard height
Double lamp socket outlet (controlled from wall switch) | 1 | (D18) Electrical Plan – Ground Floor | Standard height

## Slide 4
DOWNSTAIRS BATHROOM
LIGHTING |  |  |  |  |  |  |  |  |  |  | 
Ref ID within room | TYPE | BRAND / SUPPLIER | NAME | QUANTITY | CODE / REF | COLOUR/FINISH OPTION | DIMS (mm) | BULB | CONTROL SWITCH | REFERENCE DRAWING | ADDITIONAL INFO and WWW LINKS
16 | Ceiling Light | Marset / AllModernOutlet | Tango Lighting Flash Ceiling Lamp | 2 | N/A | Transparent, Chrome back plate | 101.6(4") H x 152.4(6") D | 1 x 60W G9 base Halogen (not included) | Dimmer switch positioned at entry point, RCD/GFCI protected and located in Bathroom Zone 3 | (D16) Reflected Ceiling Plan – Ground Floor | Product Info: http://www.allmodernoutlet.com/tango-lighting-flash-ceiling-lamp-by-marset/
17 | Wall Light | John Lewis | Kashimo Over Mirror Bathroom Light | 1 | 70230205 | Chrome | H40 x W350 x D180 | 1x 8W low energy bulb | On/Off switches: for lighting control from 2 different locations: one at entry point, and one beside sink, both RCD/GFCI protected and located in Bathroom Zone 3 (ensure appropriate height for placement outside of sink Zone 2) | (D18) Electrical Plan – Ground Floor | Product Info: http://www.johnlewis.com/kashimo-over-mirror-bathroom-light/p181637 Wall light installation height: 2000 mm
18 | Wall Light | Panache Casa | Vanity Wall | 1 | N/A | White/Pewter | Shade: 200/150 Dia. x 200 H Arm: max 700L | 1 x 50W Standard | On/Off switches: for lighting control from 2 different locations: one positioned at entry point, and one near wall light, both RCD/GFCI protected and located in Bathroom Zone 3. | (D18) Electrical Plan – Ground Floor | Product Info: http://www.panachecasa.com/vanity-wall-108 Wall light installation height: 1300 mm
ELECTRICAL |  |  | 
DESCRIPTION | QUANTITY | REFERENCE DRAWING | ADDITIONAL NOTES
Double switched socket outlet, located in Bathroom Zone 3, RCD/GFCI protected | 1 | (D18) Electrical Plan – Ground Floor | Height of outlet to ensure its positioning in Bathroom Zone 3 (outside of Sink Bathroom Zone 2)
Single switched socket outlet, located in Bathroom Zone 3, RCD/GFCI protected | 1 | (D18) Electrical Plan – Ground Floor | Standard height

## Slide 5
SITTING ROOM
LIGHTING |  |  |  |  |  |  |  |  |  |  | 
Ref ID within room | TYPE | BRAND / SUPPLIER | NAME | QUANTITY | CODE / REF | COLOUR/FINISH OPTION | DIMS (mm) | BULB | CONTROL SWITCH | REFERENCE DRAWING | ADDITIONAL INFO and WWW LINKS
24 | Chandelier | Mvos / Bobby Berk Home | Heavy Guy Chandelier | 1 | N/A | Black | 952.5 (37.5”)Dia. x 476.25(18.75”)H | 5 x 40W standard | Dimmer at entry point | (D16) Reflected Ceiling Plan – Ground Floor | Product Info: http://www.bobbyberkhome.com/product/pendant-lamps/10328-33897/heavy-guy-chandelier-in-black.html
ELECTRICAL |  |  | 
DESCRIPTION | QUANTITY | REFERENCE DRAWING | ADDITIONAL NOTES
Double switched socket outlet | 2 | (D18) Electrical Plan – Ground Floor | Standard height
Single switched socket outlet | 2 | (D18) Electrical Plan – Ground Floor | Standard height
Single lamp socket outlet (controlled from wall switch) | 3 | (D18) Electrical Plan – Ground Floor | Standard height
Floor socket | 2 | (D18) Electrical Plan – Ground Floor | -
Television Point | 1 | (D18) Electrical Plan – Ground Floor | -

## Slide 6
PLAYROOM
LIGHTING |  |  |  |  |  |  |  |  |  |  | 
Ref ID within room | TYPE | BRAND / SUPPLIER | NAME | QUANTITY | CODE / REF | COLOUR/FINISH OPTION | DIMS (mm) | BULB | CONTROL SWITCH | REFERENCE DRAWING | ADDITIONAL INFO and WWW LINKS
16 | Pendant | Anglepoise / John Lewis | Duo Maxi Pendant | 1 | 10410206 | White Shade, Red Flex | H300 x Dia. 230 Drop 900, task lighting above children’s table (max 1615) | 1 x 42W ES halogen standard bulb (not included) | Dimmer at entry point | (D16) Reflected Ceiling Plan – Ground Floor | Product Info: http://www.johnlewis.com/anglepoise-duo-maxi-pendant/p381425
17 | Pendant | Zero / Northern Icon | PXL Pendant Lamp, Saucer Shaped Version | 1 | 62327 | Multicolour | Dia. 475 x H 280 Drop 350, to allow for walking under (2500 max) | T5 circular tube 40W, 55W or E27 max 53W | On/Off switches for lighting control from 2 different locations (as shown on drawings) | (D16) Reflected Ceiling Plan – Ground Floor | Product Info: https://www.northernicon.com/p-796-pxl-pendant-lamp-50.aspx
ELECTRICAL |  |  | 
DESCRIPTION | QUANTITY | REFERENCE DRAWING | ADDITIONAL NOTES
Double switched socket outlet | 3 | (D18) Electrical Plan – Ground Floor | Standard height

## Slide 7
DINING ROOM
LIGHTING |  |  |  |  |  |  |  |  |  |  | 
Ref ID within room | TYPE | BRAND / SUPPLIER | NAME | QUANTITY | CODE / REF | COLOUR/FINISH OPTION | DIMS (mm) | BULB | CONTROL SWITCH | REFERENCE DRAWING | ADDITIONAL INFO and WWW LINKS
11 | Pendant | Limpalux | MoonJelly 510 - Lemon | 1 | M-510-L | Lemon | Ø 510 / H 250 Drop: 850, allowing for min distance to table top of 762 (30”) (2000 max drop ) | 1 x 60W max E27 | The 2 pendants are to be on the same circuit using dimmer switches for lighting control from 2 different locations (as shown on drawings) | (D16) Reflected Ceiling Plan – Ground Floor | Product info: http://www.limpalux.de/shop/MOONJELLY/510-LEMON.html
12 | Pendant | Limpalux | MoonJelly 510 - White | 1 | M-510-W | White | Ø 510 / H 250 Drop: 850, allowing for min distance to table top of 762( 30”) (2000 max) | 1 x 60W max E27 |  | (D16) Reflected Ceiling Plan – Ground Floor | Product info: http://www.limpalux.de/shop/MOONJELLY/510-WHITE.html
14 | Pendant | Possini / Lamps Plus | Possini Clear Glass Tube Mini Pendant Light | 3 | Style # N6753 | Chrome finish / Clear ribbed glass | Glass body is 38.1(1 1/2”) wide by 304.8(12”) high. Comes with 3048(10’) adjustable cord. Canopy is 120.65(4 3/4”) wide. Drop: 500 (Bottom of light at eye level for a tall person) | 1 x 20W G4 halogen bulb (included) | Dimmer switches for lighting control from 2 different locations (as shown on drawings) | (D16) Reflected Ceiling Plan – Ground Floor | Product Info: http://www.lampsplus.com/products/possini-clear-glass-tube-mini-pendant-light__n6753.html Electronic transformer included.
15 | Recessed Light | Galaxy Lighting / Lowes | Galaxy Lighting Low/Line Voltage Reflector Recessed Lighting Trim | 4 | Mfr Part # 402CH UPC# 775379028947 Group # 68564545 | Chrome/White | 123.83Ø 28.58H Can size: 101.6 (4’) | MR16 12V, max 50W GX5.3 base (req. transformer) Three Flood (F), One Narrow Flood (NF) as marked | Dimmer switches for lighting control from 2 different locations (as shown on drawings) | (D16) Reflected Ceiling Plan – Ground Floor | Product info: http://www.galaxy-lighting.com/ http://www.lowes.ca/recessed-lighting-trims_329.html?page=3
ELECTRICAL |  |  | 
DESCRIPTION | QUANTITY | REFERENCE DRAWING | ADDITIONAL NOTES
Double switched socket outlet | 3 | (D18) Electrical Plan – Ground Floor | Standard height

## Slide 8
KITCHEN
LIGHTING |  |  |  |  |  |  |  |  |  |  | 
Ref ID within room | TYPE | BRAND / SUPPLIER | NAME | QUANTITY | CODE / REF | COLOUR/FINISH OPTION | DIMS INFO (mm) | BULB | CONTROL SWITCH | REFERENCE DRAWING | ADDITIONAL INFO and WWW LINKS
28 | Pendant | CB2 | Siren | 1 | N/A | Red | Shade: 508Ø D,419.1H Canopy: 152Ø, 25.4H Cord (drop): 720 (to allow for 30” (762) distance to countertop) (2590.8L max drop) | 23 watt max SB-CFL bulb, or 100 watt max type A standard | On/Off switches for lighting control from 2 different locations: one located at entry point on wall, second on outside of oven cabinet under peninsula countertop (as shown on drawing) | (D16) Reflected Ceiling Plan – Ground Floor | Product info: http://www.cb2.com/siren-pendant-lamp/s274243 http://www.cb2.com/Assembly-Instructions/English/siren_pendant.pdf
29 | Recessed Lights, General | Galaxy Lighting / Lowes | Galaxy Lighting Low/Line Voltage Reflector Recessed Lighting Trim | 5 | Mfr Part # 402CH UPC# 775379028947 Group # 68564545 | Chrome/White | 123.83Ø 28.58H Can size: 101.6 (4’) | MR16 12V, max 50W GX5.3 base (req. transformer) Two Flood (F), Two Wide Flood (WF), One Narrow Flood (NF) | Dimmer switches for lighting control from 3 different locations (as shown on drawing) {One added at entrance from outside for maximum convenience} | (D16) Reflected Ceiling Plan – Ground Floor | Product info: http://www.galaxy-lighting.com/ http://www.lowes.ca/recessed-lighting-trims_329.html?page=3
29 | Recessed Lights, Task | Galaxy Lighting / Lowes | Galaxy Lighting Low/Line Voltage Reflector Recessed Lighting Trim | 6 | Mfr Part # 402CH UPC# 775379028947 Group # 68564545 | Chrome/White | 123.83Ø 28.58H Can size: 101.6 (4’) | MR16 12V, max 50W GX5.3 base (req. transformer) Four Spot (S), and Two Spot or Narrow Spot (S/NS) as marked | Dimmer switches for lighting control from 2 different locations (as shown on drawing) | (D16) Reflected Ceiling Plan – Ground Floor | Product info: http://www.galaxy-lighting.com/ http://www.lowes.ca/recessed-lighting-trims_329.html?page=3
Section 8 Kitchen continued on next page…

## Slide 9
KITCHEN - continued
ELECTRICAL |  |  | 
DESCRIPTION | QUANTITY | REFERENCE DRAWING | ADDITIONAL NOTES
Double switched socket outlet | 4 | (D18) Electrical Plan – Ground Floor | On walls with kitchen counters: above top edge of backsplash; Otherwise – standard height
Single switched socket outlet | 1 | (D18) Electrical Plan – Ground Floor | On the outside of oven cabinet: under peninsula countertop (as shown on drawing)
LIGHTING |  |  |  |  |  |  |  |  |  |  | 
Ref ID within room | TYPE | BRAND / SUPPLIER | NAME | QUANTITY | CODE / REF | COLOUR/FINISH OPTION | DIMS INFO (mm) | BULB | CONTROL SWITCH | REFERENCE DRAWING | ADDITIONAL INFO and WWW LINKS
30 | LED Strip Lights | Super Bright LEDs | NFLSK-UC series Under Cabinet LED Flexible Light Strip Kit, with KLUS Surface Mount Aluminum LED Profile Housing | 2 kits + 9 housings NOTE: The 2 kits have a total strip length of 2x5000=10000m. Length needed for Kitchen application is 6340 mm. The remaining length of 3660 mm is to be used for the 2 closets in the Children’s Room (Section 10) and Guest Room (Section 11), to make 4 strips (2 for each room, each 900L). | NFLSK-UC Housing part#: B5390 | Copper, Aluminum housing Diffused lens cover | Total length of cabinets/shelves to apply to: 6340; For length breakdown please see ADDITIONAL NOTES. strip W=8, total H=2 Housing: W=15, H=6 Housing to be cut to size for each section. | LED 4500K color temperature, Natural White | On/off switches for lighting control from 2 different locations (as shown on drawing) | (D18) Electrical Plan – Ground Floor | Product info and installation instructions: http://www.superbrightleds.com/moreinfo/top-emitting/nflsk-uc-series-under-cabinet-led-flexible-light-strip-kit/1426/ A 12-Volt DC power supply is included. Please ensure that the latter as well as all cabling are to be properly concealed out of view. See exact placements and lengths in the Reflected Ceiling Plan – Ground Floor Drawing. Lengths (as close as cut indicating dashed lines allow): 2x990 – for bottom of lower large Akurum wall cabinets + 1x760 – top bottom of small Akurum cabinet + 6x600 – bottom of LIMHAMN wall shelves.

## Slide 10
SHOWER ROOM
LIGHTING |  |  |  |  |  |  |  |  |  |  | 
Ref ID within room | TYPE | BRAND / SUPPLIER | NAME | QUANTITY | CODE / REF | COLOUR/FINISH OPTION | DIMS (mm) | BULB | CONTROL SWITCH | REFERENCE DRAWING | ADDITIONAL INFO and WWW LINKS
19 | Flush Ceiling Light | Astro / John Lewis | Astro Arezzo Flush Bathroom Ceiling Light | 2 | 10504509 | Glass | H190 x Dia.230 | 1 x 42W ES classic | Dimmer switch positioned at entry point, outside of the Shower Room (as shown on drawing) | (D17) Reflected Ceiling Plan – First Floor | Product Info: http://www.johnlewis.com/231744035/Product.aspx
20 | Wall Light | John Lewis | Kashimo Over Mirror Bathroom Light | 2 | 70230205 | Chrome | H40 x W350 x D180 | 1x 8W low energy bulb | On/off switches for lighting control from 2 different locations, one positioned outside of the Shower Room, and the second one RCD/GFCI protected positioned between sinks in Bathroom Zone 3 (ensure appropriate height for placement outside of sink Zones 2) | (D19) Electrical Plan – First Floor | Product Info: http://www.johnlewis.com/kashimo-over-mirror-bathroom-light/p181637 Wall lights installation height: 2000 mm.
21 | Recessed Low Voltage Downlight | Saxby Lighting | Shield LV IP65 50W | 1 | DLF805C | Chrome, Clear Glass | 130H x 86 Dia. x 5 Projection Cut Out : 66 Diameter | 1 x 50W GU5.3 MR16 reflector (included) | Dimmer switch, RCD/GFCI protected positioned in Bathroom Zone 3 inside the Shower Room for proximity convenience (ensure appropriate height for placement outside of sink Zone 2) | (D17) Reflected Ceiling Plan – First Floor | Product Info: http://www.saxbylighting.com/index.php?pg=details&prod=1347
ELECTRICAL |  |  | 
DESCRIPTION | QUANTITY | REFERENCE DRAWING | ADDITIONAL NOTES
Single switched socket outlet | 2 | (D19) Electrical Plan – First Floor | Height of outlets to ensure their positioning in Bathroom Zone 3 (outside of Sink Bathroom Zone 2)

## Slide 11
CHILDREN’S BEDROOM
LIGHTING |  |  |  |  |  |  |  |  |  |  | 
Ref ID within room | TYPE | BRAND / SUPPLIER | NAME | QUANTITY | CODE / REF | COLOUR/FINISH OPTION | DIMS (mm) | BULB | CONTROL SWITCH | REFERENCE DRAWING | ADDITIONAL INFO and WWW LINKS
14 | Chandelier | Brickell Collection | Exploding Chandelier | 1 | N/A | Chrome | 584.2(23") W x 584.2(23") H x 584.2(23") D Drop 350, to allow for walking under | Standard 40W max | Dimmer switches for lighting control from 2 different locations (as shown on drawing) | (D17) Reflected Ceiling Plan – First Floor | Product Info: http://brickellcollection.com/exploding-chandelier/
15 | Wall light *See ADDITIONAL INFO >>>>>>> | Jonathan Adler / YLighting | Havana Wall Swinger by Jonathan Adler | 2 | Item #: ROB-x695 | Polished Nickel, Powder Coat White | Overall: 222.25(8.75”)-387.35(15.25”) Adjustable H X 142.24(5.6”)-755.65(29.75”) Adjustable W Shade: 76.2(3”) X 127(5”) X 209.55(8.25”) | 1 X 60W medium base incandescent (not included) | Plugged into lamp sockets controlled by a wall switch positioned at entry point; Each lamp has its own local switch | Lamp sockets shown on (D19) Electrical Plan - First Floor | Product Info: http://www.ylighting.com/robert-abbey-w695.html To be installed “pin-up”, and plugged into the lighting circuit. Height: Comfortable for reading above each bed: above lower bunk @ H930 mm, above top bunk @ H1650 mm (bottom of light shade to level at just above person’s shoulder (or at person’s chin) when sitting in bed in reading position). Also see Furnishing Layout – First Floor drawing for positioning. May be installed by the decorators (included here for clarity).
Section 10 Children’s Bedroom continued on next page…

## Slide 12
CHILDREN’S BEDROOM - continued
LIGHTING |  |  |  |  |  |  |  |  |  |  | 
Ref ID within room | TYPE | BRAND / SUPPLIER | NAME | QUANTITY | CODE / REF | COLOUR/FINISH OPTION | DIMS (mm) | BULB | CONTROL SWITCH | REFERENCE DRAWING | ADDITIONAL INFO and WWW LINKS
17 | LED Strip Lighting | Super Bright LEDs | Extra strips remaining from under-cabinet kitchen installation are to be used. Please see Section 8 for more info. KLUS Surface Mount Aluminum LED Profile Housing | 2 x 900L (both strip and housing) | NFLSK-UC Housing part#: B5390 | Copper, Aluminum housing Diffused lens cover | Each strip: 900 cut length (as close as cut indicating dashed lines allow); Strip: W=8, total H=2 Housing: W=15, H=6 | LED 4500K color temperature, Natural White | Switch with pilot lamp | (D17) Reflected Ceiling Plan - First Floor | Product Info: http://www.superbrightleds.com/moreinfo/top-emitting/nflsk-uc-series-under-cabinet-led-flexible-light-strip-kit/1426/ Requires 12VDC CPS series Power Supply (from manufacturer). The 2 strips are to be installed parallel to each other, see drawing for placement. To be installed inside housing with diffused lens cover: http://www.superbrightleds.com/moreinfo/led-strips-and-bars/klus-b5390--eco-series-surface-mount-aluminum-led-profile-housing-tami/1559/3682/
ELECTRICAL |  |  | 
DESCRIPTION | QUANTITY | REFERENCE DRAWING | ADDITIONAL NOTES
Double switched socket outlet | 3 | (D19) Electrical Plan – First Floor | Standard height
Single lamp socket outlet (controlled from wall switch) | 3 | (D19) Electrical Plan – First Floor | Standard height

## Slide 13
GUEST ROOM
LIGHTING |  |  |  |  |  |  |  |  |  |  | 
Ref ID within room | TYPE | BRAND / SUPPLIER | NAME | QUANTITY | CODE / REF | COLOUR/FINISH OPTION | DIMS (mm) | BULB | CONTROL SWITCH | REFERENCE DRAWING | ADDITIONAL INFO and WWW LINKS
16 | Chandelier | Aromas Del Campo | Cohen 5 | 1 | C1122-5 | Negro Brillo | 600 Diam. Drop 800, to allow for getting in and out of bed and sitting on bed comfortably (1500 max drop) | 5 x E-27, 60W (not included) | Dimmer switches for lighting control from 2 different locations (as shown on drawings); Height: 1000 mm to allow for access from sitting in bed. | (D17) Reflected Ceiling Plan – First Floor | Product Info: http://www.aromasdelcampo.com/en/project/c11225-cohen/
17 | Wall Light | Aromas Del Campo | Cohen | 3 | A1122 | Negro Brillo | 300D x 70H; 120 plate diameter | Max 60W or 15W CFL | Main On/Off wall switch at entry point to control all 3 wall lights simultaneously; Each light is to have its individual switch as well. | (D19) Electrical Plan – First Floor | Product Info: http://www.aromasdelcampo.com/en/project/a1122-cohen/ Wall lights installation height: 1150 mm (Allowing for min 610 mm (approx. 24”) height above nightstand (which is 520 mm tall)).
Section 11 Guest Room continued on next page…

## Slide 14
GUEST ROOM - continued
LIGHTING |  |  |  |  |  |  |  |  |  |  | 
Ref ID within room | TYPE | BRAND / SUPPLIER | NAME | QUANTITY | CODE / REF | COLOUR/FINISH OPTION | DIMS (mm) | BULB | CONTROL SWITCH | REFERENCE DRAWING | ADDITIONAL INFO and WWW LINKS
18 | LED Strip Lighting | Super Bright LEDs | Extra strips remaining from under-cabinet kitchen installation are to be used. Please see Section 8 for more info. KLUS Surface Mount Aluminum LED Profile Housing | 2 x 900L (both strip and housing) | NFLSK-UC Housing part#: B5390 | Copper, Aluminum housing Diffused lens cover | Each strip: 900 cut length (as close as cut indicating dashed lines allow); Strip: W=8, total H=2 Housing: W=15, H=6 | LED 4500K color temperature, Natural White | Switch with pilot lamp | (D17) Reflected Ceiling Plan - First Floor | Product Info: http://www.superbrightleds.com/moreinfo/top-emitting/nflsk-uc-series-under-cabinet-led-flexible-light-strip-kit/1426/ Requires 12VDC CPS series Power Supply (from manufacturer). The 2 strips are to be installed parallel to each other, see drawing for placement. To be installed inside housing with diffused lens cover: http://www.superbrightleds.com/moreinfo/led-strips-and-bars/klus-b5390--eco-series-surface-mount-aluminum-led-profile-housing-tami/1559/3682/
ELECTRICAL |  |  | 
DESCRIPTION | QUANTITY | REFERENCE DRAWING | ADDITIONAL NOTES
Double switched socket outlet | 2 | (D19) Electrical Plan – First Floor | Standard height
Single switched socket outlet | 2 | (D19) Electrical Plan – First Floor | Standard height

## Slide 15
MASTER BEDROOM
LIGHTING |  |  |  |  |  |  |  |  |  |  | 
Ref ID within room | TYPE | BRAND / SUPPLIER | NAME | QUANTITY | CODE / REF | COLOUR/FINISH OPTION | DIMS (mm) | BULB | CONTROL SWITCH | REFERENCE DRAWING | ADDITIONAL INFO and WWW LINKS
23 | Pendant | Studio Italia Design / YLighting | Tris SO1 | 2 | N/A | Chrome / Black Glass | 600 Diam. Drops: For the one above bed: 860, allowing for getting in and out of bed and sitting on bed comfortably; For the one in Dressing Area: 350, allowing for walking under (max drop 2000) | 6 X 60W G9 halogen | Dimmer switches for lighting control from 4 different locations (as shown on drawings); The 2 control switches located at bedside to be at height 900 (to top of plate) mm to allow for access from sitting in bed. | (D17) Reflected Ceiling Plan – First Floor | Product Info: http://www.ylighting.com/sid-tris-s.html http://www.sid-usa.com/prod2.php?nombre=TRIS&subtipo=SO1 Pendants position: one above bed in Sleeping Area, one is Dressing Area. The switches
24 | Pendant | Studio Italia Design / YLighting | Tris SO2 | 2 | N/A | Chrome / Black Glass | 360 Diam. Drop: 350 for both, allowing for walking under (max drop 2000) | 3 X 40W, G9 halogen | Dimmer switches for lighting control from 2 different locations (as shown on drawings) | (D17) Reflected Ceiling Plan – First Floor | Product Info: http://www.ylighting.com/sid-tris-s.html http://www.sid-usa.com/prod2.php?nombre=TRIS&subtipo=SO2 These 2 pendants are to illuminate the pathway from the Master Bedroom Entrance to the balcony door. The switch at balcony entrance to be located below window sill as location allows.
25 | LED Wall Lamp *See ADDITIONAL INFO >>>>>>> | IKEA | IKEA PS 2012 | 2 | 002.117.00 | Black | Max. length: 900 Max. width: 550 Height: 300 Cord length: 2400 | Built-in LED light source, 2700 K, Warm White | Plugged into lamp sockets controlled by wall switches in 2 different locations (one at outside entry point, and one inside the room for easy access once door is closed from the inside). Each lamp to have its own local switch as well. | Lamp sockets shown on (D19) Electrical Plan - First Floor | Product Info: http://www.ikea.com/ca/en/catalog/products/00211700/ Not to be hardwired. Installation height: 850 mm (floor to mid-base, with min height above low nightstand allowed). Please see Master Bedroom Elevation MB1and Furnishing Layout – First Floor drawing for positioning. May be installed by the decorators (included here for clarity).
ELECTRICAL |  |  | 
DESCRIPTION | QUANTITY | REFERENCE DRAWING | ADDITIONAL NOTES
Double switched socket outlet | 4 | (D19) Electrical Plan – First Floor | Standard height.
Single switched socket outlet | 4 | (D19) Electrical Plan – First Floor | The ones at the bedside tables to be positioned at height of 150 mm to allow them to be hidden out of view behind the low sitting bed frame. All others at standard height.
Single lamp socket outlet (controlled from wall switch) | 5 | (D19) Electrical Plan – First Floor | 

## Slide 16
ENSUITE BATHROOM
LIGHTING |  |  |  |  |  |  |  |  |  |  | 
Ref ID within room | TYPE | BRAND / SUPPLIER | NAME | QUANTITY | CODE / REF | COLOUR/FINISH OPTION | DIMS (mm) | BULB | CONTROL SWITCH | REFERENCE DRAWING | ADDITIONAL INFO and WWW LINKS
17 | Pendant | John Lewis | Celeste Small | 2 | 70143009 | Silver, Glass | H220 x W250 x D220, Drop 500 (Bottom of light at eye level for a tall person) (Max drop 1100) | 1 x 40W Max ES Gls Standard 'a' | Dimmer switches for control from 2 different locations, both RCD/GFCI protected and located in Bathroom Zone 3, one at entry and one between sinks (ensure appropriate height for placement outside of sink Zones 2) | (D17) Reflected Ceiling Plan – First Floor | Product Info: http://www.johnlewis.com/john-lewis-celeste-silver-small/p231656747
18 | Flush Ceiling Light | John Lewis | Torus | 1 | 10505010 | Chrome, White Acrylic | H105 x Dia.345 | 1 x 2GX13 fluorescent circular bulb | Not dimmable. On/off switch at entry point RCD/GFCI protected and located in Bathroom Zone 3 (as shown on drawing) | (D17) Reflected Ceiling Plan – First Floor | Product Info: http://www.johnlewis.com/john-lewis-torus-flush-bathroom-ceiling-light/p231744065
19 | Recessed Low Voltage Downlight | Saxby Lighting | Shield LV IP65 50W | 2 | DLF805C | Chrome, Clear Glass | 130H x 86 Dia. x 5 Projection Cut Out : 66 Diameter | 1 x 50W GU5.3 MR16 reflector (included) | Dimmer switch positioned near entry point, RCD/GFCI protected and located in Bathroom Zone 3. | (D17) Reflected Ceiling Plan – First Floor | Product Info: http://www.saxbylighting.com/index.php?pg=details&prod=1347
ELECTRICAL |  |  | 
DESCRIPTION | QUANTITY | REFERENCE DRAWING | ADDITIONAL NOTES
Single switched socket outlet | 2 | (D19) Electrical Plan – First Floor | Height of outlets to ensure their positioning in Bathroom Zone 3 (outside of Sink Bathroom Zone 2)

## Slide 17
PATIO
LIGHTING |  |  |  |  |  |  |  |  |  |  | 
Ref ID within room | TYPE | BRAND / SUPPLIER | NAME | QUANTITY | CODE / REF | COLOUR/FINISH OPTION | DIMS (mm) | BULB | CONTROL SWITCH | REFERENCE DRAWING | ADDITIONAL INFO and WWW LINKS
11 | Outdoor Pendant | Troy Lighting | Nautilus | 2 | F2267EB | English Bronze / Glass | 260.35(10 1/4”)W x 333.38(13.125”)H | 1 x 60 watt Candelabra bulb incandescent | Dimmer switches for lighting control from 2 different locations (as shown on drawings). The outside dimmer to be weatherproof (WP); the inside dimmer to be positioned under window sill as location allows. | (D16) Reflected Ceiling Plan – Ground Floor | Product Info: http://www.troylightinglights.com/product/troy-lighting-nautilus-outdoor-pendants-chandeliers-f2267eb.html
ELECTRICAL |  |  | 
DESCRIPTION | QUANTITY | REFERENCE DRAWING | ADDITIONAL NOTES
Double switched socket outlet – Weatherproof (WP) | 2 | (D18) Electrical Plan – Ground Floor | Standard height

## Slide 18
BALCONY
LIGHTING |  |  |  |  |  |  |  |  |  |  | 
Ref ID within room | TYPE | BRAND / SUPPLIER | NAME | QUANTITY | CODE / REF | COLOUR/FINISH OPTION | DIMS (mm) | BULB | CONTROL SWITCH | REFERENCE DRAWING | ADDITIONAL INFO and WWW LINKS
7 | Exterior Wall Light | Access Lighting / Lumens | Nauticus | 2 | 20291-BL/FST (R277218) | Black, Frosted Glass | Height 107.95(4.25”) Width 209.55(8.25”) Depth 88.9(3.5”) | One 60 Watt Type E26 Medium Base Incandescent lamp (not included). | Dimmer switch positioned inside near balcony door, under window sill, as location allows. | (D19) Electrical Plan – First Floor | Product Info: http://www.lumens.com/nauticus-ceiling/wall-by-access-lighting-uu372096.html Height for wall lights installation: 1700 mm
ELECTRICAL |  |  | 
DESCRIPTION | QUANTITY | REFERENCE DRAWING | ADDITIONAL NOTES
Double switched socket outlet – Weatherproof (WP) | 2 | (D19) Electrical Plan – First Floor | Standard height